## Sheet1
JIT Hotel BMS IO Sheet | [7 empty] | FIELD DEVICS
QTY | System | Function | DI | AI | DO | AO | Device | ADPS | CO | WLS | FLS | RTS
DDC-01
10 | VRF OUTDOOR UNITS | Modbus integration |  |  |  |  | Modbus Controller
117 | INDOOR UNITS | Fan Run Status | 117 |  |  |  | Air Diff Pressure Switch | 117
|  | Fan Trip Status | 117 |  |  |  | Voltage free contact
|  | Fan Start/Stop |  |  | 117 |  | Voltage free contact
1 | PRESSURIZATION FAN | FAN RUN STATUS | 1 |  |  |  | Air Diff Pressure Switch | 1
|  | Fan swith position | 1 |  |  |  | Voltage free contact
|  | Fan trip | 1 |  |  |  | Voltage free contact
|  | Fan start/stop |  |  | 1 |  | Voltage free contact
4 | INDOOR SPLIT UNITS | FAN RUN STATUS | 4 |  |  |  | Air Diff Pressure Switch | 4
|  | Fan swith position | 4 |  |  |  | Voltage free contact
|  | Fan trip | 4 |  |  |  | Voltage free contact
|  | Fan start/stop |  |  | 4 |  | Voltage free contact
1 | AIR CURTAINS | System On status | 1 |  |  |  | Voltage free contact
|  | System Fault Status | 1 |  |  |  | Voltage free contact
1 | Fresh Air AHU | Supply fan run status | 1 |  |  |  | Air Diff Pressure Switch | 1
|  | Fan swith position | 1 |  |  |  | Voltage free contact
|  | Fan trip | 1 |  |  |  | Voltage free contact
|  | Filter Status | 1 |  |  |  | Air Diff Pressure Switch | 1
|  | Supply Air Temperature |  | 1 |  |  | Duct Temp Sensor
|  | Supply air quality |  | 1 |  |  | Duct VOC sensor
|  | Fan start/stop |  |  | 1 |  | Voltage free contact
1 | SUPPLY FANS | FAN RUN STATUS | 1 |  |  |  | Air Diff Pressure Switch | 7
|  | Fan swith position | 1 |  |  |  | Voltage free contact
|  | Fan trip | 1 |  |  |  | Voltage free contact
|  | Fan Trip in case of fire |  |  | 1 |  | Voltage free contact
|  | Fan start/stop |  |  | 1 |  | Voltage free contact
12 | VENTILLATION & EXTRACT FAN | FAN RUN STATUS | 12 |  |  |  | Air Diff Pressure Switch | 12
|  | Fan swith position | 12 |  |  |  | Voltage free contact
|  | Fan trip | 12 |  |  |  | Voltage free contact
|  | Air quality Status |  |  |  |  | Space CO Sensor |  | 0
|  | Fan start/stop |  |  | 12 |  | Voltage free contact
2 | KITCHEN SUUPLY & EXTRACT | FAN RUN STATUS | 2 |  |  |  | Air Diff Pressure Switch | 2
| FANS | Fan swith position | 2 |  |  |  | Voltage free contact
|  | Fan trip | 2 |  |  |  | Voltage free contact
|  | Fan start/stop |  |  | 2 |  | Voltage free contact
1 | SMOKE EXTRACT FAN | FAN RUN STATUS | 1 |  |  |  | Air Diff Pressure Switch | 1
|  | Fan swith position | 1 |  |  |  | Voltage free contact
|  | Fan trip | 1 |  |  |  | Voltage free contact
|  | Fan start/stop |  |  | 1 |  | Voltage free contact
2 | BOOSTER PUMPS | Pump run status | 2 |  |  |  | Voltage free contact
|  | Pump start/stop |  |  | 2 |  | Voltage free contact
|  | Pump trip | 2 |  |  |  | Voltage free contact
|  | Pump switch position | 2 |  |  |  | Voltage free contact
DDC-02
1 | FIRE PUMP SET | Jockey pump ON status | 1 |  |  |  | Voltage free contact
|  | Diesel pump ON status | 1 |  |  |  | Voltage free contact
|  | Electric pump ON status | 1 |  |  |  | Voltage free contact
|  | Jockey pump trip | 1 |  |  |  | Voltage free contact
|  | Diesel pump trip | 1 |  |  |  | Voltage free contact
|  | Electric pump trip | 1 |  |  |  | Voltage free contact
|  | Tank Low Level | 1 |  |  |  | Water level switch |  |  | 1
|  | Tank High Level | 1 |  |  |  | Water level switch |  |  | 1
3 | WATER TANKS | High Level alarm | 3 |  |  |  | Water level switch |  |  | 3
|  | Low level alarm | 3 |  |  |  | Water level switch |  |  | 3
DDC-03
1 | LV BOARD METERS | MODBUS Integration |  |  |  |  | Modbus controller
1 | UPS | MODBUS Integration
1 | GENERATORS | Breaker On/Off | 1 |  |  |  | Voltage free contact
|  | MCCP trip status | 1 |  |  |  | Voltage free contact
|  | Common alarm | 1 |  |  |  | Voltage free contact
|  | Not in auto mode | 1 |  |  |  | Voltage free contact
| Fuel Tank | Fuel Level |  | 1 |  |  | Fuel Level sensor |  |  |  | 1
|  | Fuel transfer pump status | 1 |  |  |  | Voltage free contact
|  | Battery status | 1 |  |  |  | Voltage free contact
|  | Room Temperature |  | 1 |  |  | Room Temp Sensor |  |  |  |  | 1
2 | LIFTS | Power supply status | 2 |  |  |  | Voltage free contact
|  | Common alarm | 2 |  |  |  | Voltage free contact
|  | Cabin call alarm | 2 |  |  |  | Voltage free contact
1 | FIRE ALARM | System Fault | 1 |  |  |  | Voltage free contact
|  | System Alarm |  | 1 |  |  | Voltage free contact
| SERVER ROOM | Room Temperature |  | 1 |  |  | Room Temp Sensor |  |  |  |  | 1
|  | TOTAL | 336 | 6 | 142 | 0 |  | 146 | 0 | 8 | 1 | 2